## Sheet1
Hex Command | Command Description | Example return HEX | Example return ASCII
01 | Get Model | 53 50 4D 32 4B 0D 0A | SPM2K
9F D2 | ?(Maybe running mode?) | 45 0D 0A | E
39 | ? | 46 46 0D 0A | FF
7E | ? | 30 30 0D 0A | 00 | 9F D2 Possible Value
9F D2 | Running Mode | 45 0D 0A | E | E | Eco
4C | Input Line Volt | 32 32 30 2E 39 0D 0A | 220.9 | L | Line mode
9F D3 | Input Line Freq | 35 30 2E 30 0D 0A | 50.0 | Y | Bypass mode
4F | Output Line Volt | 32 32 31 2E 30 0D 0A | 221.0 | T | Battery test mode
46 | Output Line Freq | 34 39 2E 39 36 0D 0A | 49.96 | B | Battery mode
2F | Input Line Load Current | 30 32 2E 32 33 0D 0A | 02.23
50 | Power load % Relative to the capacity of the UPS | 30 32 35 2E 30 0D 0A | 025.0
5C | Apparent load power(Output load as percentage of full rated load) | 30 32 33 2E 30 30 0D 0A | 023.00
43 | UPS Temp. | 30 33 35 2E 36 0D 0A | 035.6
9F D9 | ?(looks like status flag but no doc for that) | 30 31 30 30 30 30 30 30 30 30 30 30 30 30 30 30 0D 0A | 0100000000000000
66 | Battery Level | 30 30 33 2E 30 0D 0A | 003.0
42 | Battery Volt | 30 35 31 2E 32 0D 0A | 051.2
6A | Estimated runtime(minutes) | 30 30 30 30 33 3A 0D 0A | 00003:
3E | Battery packs | 30 30 31 0D 0A | 001
9F D4 | Battery Current | 30 31 2E 30 0D 0A | 01.0
9F D5 | Phace Lock Flag | 31 0D 0A | 1=Locked 0=Not Locked
9F E2 |  | 4F 46 46 0D 0A | OFF
58 | Self Test Result | 4F 4B 0D 0A | NO
9F E3 | UPS Alarm | 4F 4E 0D 0A | ON
9F E4 | Alarm at Bypass mode | 4F 4E 0D 0A | ON
9F E5 | Auto Reboot | 4F 4E 0D 0A | ON
9F E6 | Bypass when ups is off | 4F 4E 0D 0A | ON
9F E7 | Converter Mode | 4F 46 46 0D 0A | OFF
9F E8 | Eco Mode | 4F 4E 0D 0A | ON
9F E9 | Green power function | 4F 4E 0D 0A | ON
9F EA | Cold Start | 4F 4E 0D 0A | ON
9F EB | Bypass not allowed | 4F 4E 0D 0A | ON
9F BF |  | 4E 41 0D 0A | NA
75 | Upper transfer voltage (UPS goes on battery after voltage rises above this point) | 32 36 34 0D 0A | 264
6C | Low transfer voltage(UPS goes on battery after voltage drops below this point) | 31 37 36 0D 0A | 176
9F D6 | Transfer Minimum Freq and Max Freq | 34 37 2E 30 2C 35 33 2E 30 0D 0A 4E 41 0D 0A | 47.0,53.0 NA
9F D1 | UPS Rated Info(Rated VA, Rated Input Volt?, Rated Output Volt?, Rated Output Freq, Rated Battery Capacity(in ah), Rated battery Volt,???) | 30 32 30 30 30 2C 32 32 30 2C 32 32 30 2C 35 30 2E 30 2C 30 30 39 2C 30 34 38 2E 30 2C 31 31 0D 0A | 02000,220,220,50.0,009,048.0,11
9F D7 | Voltage Range for ECO Mode | 32 30 39 2C 32 33 31 0D 0A | 209,231
9F F3 | Unit Battery Capaticy(Ah)
59 | Enter smart mode This must be sent before anything else on this page will work. | 53 4D 0D 0A | SM
63 | Writable variable Up to 8 letter identifier for keeping track of your hardware | 55 50 53 5F 49 44 45 4E 0D 0A | UPS_IDEN
62 | Firmware revision | 34 33 36 2E 30 38 42 54 2E 49 0D 0A | 436.08BT.I
1A | Capability string | 23 75 49 34 33 32 33 31 32 34 32 32 35 33 32 36 34 6C 49 34 33 31 38 37 31 37 36 31 36 35 31 35 34 65 34 34 32 30 30 31 35 35 30 39 30 6F 34 33 33 32 32 30 32 33 30 32 34 30 71 34 34 32 30 32 30 35 30 37 31 30 70 34 34 33 30 32 30 31 38 30 33 30 30 36 30 30 6B 34 34 31 30 54 4C 4E 72 34 34 33 30 30 30 30 36 30 31 38 30 33 30 30 77 34 34 32 4E 4F 30 32 30 35 30 38 45 34 34 33 33 33 36 31 36 38 4F 4E 20 4F 46 46 F0 34 35 35 41 55 54 4F 20 36 30 2F 2E 31 36 30 2F 33 20 35 30 2F 2E 31 35 30 2F 33 20 0D 0A | #uI43231242253264lI43187176165154e44200155090o433220230240q44202050710p443020180300600k4410TLNr443000060180300w442NO020508E443336168ON OFF?55AUTO 60/.160/3 50/.150/3 n9S2331A01894 x08/05/23
6E | Serial number | 39 53 32 33 33 31 41 30 31 38 39 34 0D 0A | 9S2331A01894
78 | Last battery change | 30 38 2F 30 35 2F 32 33 0D 0A | 08/05/23
39 | Line Quality (does not return with cr/lf) | 00/FF | 00=unacceptable,ff=acceptable
51 | Status flag(binary, see table below) e.g. 08 = on line, battery OK 10 = on battery, battery OK | 30 38 0d 0a
Bit | Meaning
0 | 1
= runtime calibration occurring
Not reported by Smart UPS v/s and BackUPS Pro
1 | 1
= SmartTrim
Not reported by 1st and 2nd generation SmartUPS models
2 | 1
= SmartBoost
3 | 1
= on line
4 | 1
= on battery
5 | 1
= overloaded output
6 | 1
= battery low
7 | 1
= replace battery

## Sheet2
Device Descriptor
Configuration Descriptor
Interface Descriptor
Endpoint Descriptor
HID Descriptor
Report Descriptor